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Part 1. PRODUCT(S) - Indoor Units (Multi Zone Systems)
Wall Mounted – High Efficiency <KNMAB071A><KNMAB151A><KNMAB241A>
<KNUAB091A><KNUAB121A><KNUAB181A>
0. Operating Conditions
The indoor unit shall be capable of the following ambient operating range.
Cooling: 57°F DB to 77°F WB
Heating: 59°F WB to 81°F DB
General
0. Unit shall be manufactured by LG.
Unit shall be factory assembled, wired, piped and run tested.
Unit shall be designed to be installed for indoor application.
Unit shall be attached to an installation plate/bracket that secures unit to the wall.
The depth of the unit shall not exceed 9 inches.
Casing/Panel 
0. Unit case shall be manufactured of heavy duty Acrylonitrile Butadiene Styrene (ABS) and High Impact Polystyrene (HIPS) plastic. 
Unit case shall have a pearl white finish: Munsell 7.5BG 10/2 (RAL 9016).
The front surface of the unit shall have an architectural curved panel with pearl white finish and integrated digital display.
Cabinet Assembly
0. Unit shall have one supply air outlet and one return air inlet.
Unit shall be equipped with factory installed temperature thermistors for 
Return air
Refrigerant entering coil
Refrigerant leaving coil
Unit shall have a built-in control panel to communicate with the outdoor unit.
Unit shall have the following functions as standard
Self-diagnostic function 
Auto restart function
Auto operation function
Auto clean function
Dehumidifying function
Forced operation
Hot Start
Sleep mode
Unit shall be capable of refrigerant piping in 4 different directions.
Unit shall be capable of drain piping in 2 different directions.
Fan Assembly
0. The unit shall have a direct drive, cross flow fan made of high strength ABS plastic.
The fan motor is Brushless Digitally controlled (BLDC) with permanently lubricated and sealed ball bearings.
The fan/motor assembly shall be mounted on vibration attenuating rubber grommets.
The fan speed shall be controlled using microprocessor based direct digitally controlled algorithm.
In cooling mode, the indoor fan shall have the following settings: Low, Med, High, Jet Cool, and Auto.
In heating mode, the indoor fan shall have the following settings: Low, Med, High, Jet Heat and Auto.
The Auto fan setting shall adjust the fan speed to most effectively achieve the set-point.
Unit shall have factory installed motorized louver to provide flow of air in up and down direction for uniform airflow.
Unit shall have factory installed motorized guide vane to control the direction of flow of air from side to side.
Filter Assembly
0. The return air inlet shall have a factory supplied primary removable, washable filter.
The unit shall be equipped with factory supplied secondary 3M Micro Dust Filter.
The filter access shall be from the front of the unit.
Coil Assembly
0. Unit shall have a factory built coil comprised of aluminum fins mechanically bonded on copper tubing.
Unit shall have minimum of 2 rows of coils.
Unit shall have a factory supplied condensate drain pan below the coil.
Unit shall be designed for gravity drain.
Unit shall have a factory insulated drain hose to handle condensate.
Unit shall have provision of 45° flare refrigerant pipe connections.
The coil shall be factory pressure tested at a minimum of 626 psig.
All refrigerant piping from outdoor unit to indoor unit shall be field insulated.
Microprocessor Control
0. The unit shall have a factory installed microprocessor controller capable of performing functions necessary to operate the system.
Systems are designed for and intended to operate with an LG proprietary controller to achieve full variable-speed performance and rated efficiencies.
The indoor unit shall be able to communicate with the outdoor unit using a field supplied minimum of 18 AWG, 2-conductor, stranded, shielded or unshielded communication cable.  If shielded, it must be grounded to chassis at ODU only.
Central control shall be available through a terminal connection on the outdoor unit.
Group control shall be available to allow multiple indoor units to operate from a single LG controller, or allow connection of more than one LG controller to an indoor unit.
The unit controls shall operate the indoor unit using one of the five operating modes:
Auto operation
Heating
Cooling
Dry
Fan only
Electrical
0. The unit electrical power shall be 208-230/1/60 (V/Ph/Hz)
The unit shall be capable of operating within voltage limits of +/- 10% of the rated voltage.
Controls
0. The indoor unit shall be supplied with a wireless handheld controller.
An optional LG wired controller shall be available as an additional accessory.
An optional dry contact shall be available as an additional accessory.
The indoor unit shall have built-in (factory installed) Wi-Fi to allow monitoring and control through a smart device with the LG Smart ThinQ© application.
The indoor unit shall have a factory installed R32 refrigerant leak detection sensor designed to communicate with mitigation devices and 3rd party alarms and transmit a system error code upon detection of a refrigerant leak or sensor failure/expiration.
An optional single-port shutoff valve shall be available as an additional accessory.  The shutoff valve shall be designed to integrate with and respond to a signal from a connected R32 refrigerant leak detection sensor, to close the refrigerant valve upon receiving a signal that a refrigerant leak has been detected, or that the sensor has incurred a failure or reached its 10-year expiration date.
Warranty 
0. Please refer to the respective outdoor unit for applicable warranty.
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