Guide Specifications

# PRODUCT(S) - Indoor Units (Multi Zone Systems)

## Wall Mounted – High Efficiency <KNMAB071A><KNMAB151A><KNMAB241A>
<KNUAB091A><KNUAB121A><KNUAB181A>

### Operating Conditions

#### The indoor unit shall be capable of the following ambient operating range.

##### Cooling: 57°F DB to 77°F WB

##### Heating: 59°F WB to 81°F DB

### General

#### Unit shall be manufactured by LG.

#### Unit shall be factory assembled, wired, piped and run tested.

#### Unit shall be designed to be installed for indoor application.

#### Unit shall be attached to an installation plate/bracket that secures unit to the wall.

#### The depth of the unit shall not exceed 9 inches.

### Casing/Panel

#### Unit case shall be manufactured of heavy duty Acrylonitrile Butadiene Styrene (ABS) and High Impact Polystyrene (HIPS) plastic.

#### Unit case shall have a pearl white finish: Munsell 7.5BG 10/2 (RAL 9016).

#### The front surface of the unit shall have an architectural curved panel with pearl white finish and integrated digital display.

### Cabinet Assembly

#### Unit shall have one supply air outlet and one return air inlet.

#### Unit shall be equipped with factory installed temperature thermistors for

##### Return air

##### Refrigerant entering coil

##### Refrigerant leaving coil

#### Unit shall have a built-in control panel to communicate with the outdoor unit.

#### Unit shall have the following functions as standard

##### Self-diagnostic function

##### Auto restart function

##### Auto operation function

##### Auto clean function

##### Dehumidifying function

##### Forced operation

##### Hot Start

##### Sleep mode

#### Unit shall be capable of refrigerant piping in 4 different directions.

#### Unit shall be capable of drain piping in 2 different directions.

### Fan Assembly

#### The unit shall have a direct drive, cross flow fan made of high strength ABS plastic.

#### The fan motor is Brushless Digitally controlled (BLDC) with permanently lubricated and sealed ball bearings.

#### The fan/motor assembly shall be mounted on vibration attenuating rubber grommets.

#### The fan speed shall be controlled using microprocessor based direct digitally controlled algorithm.

#### In cooling mode, the indoor fan shall have the following settings: Low, Med, High, Jet Cool, and Auto.

#### In heating mode, the indoor fan shall have the following settings: Low, Med, High, Jet Heat and Auto.

#### The Auto fan setting shall adjust the fan speed to most effectively achieve the set-point.

#### Unit shall have factory installed motorized louver to provide flow of air in up and down direction for uniform airflow.

#### Unit shall have factory installed motorized guide vane to control the direction of flow of air from side to side.

### Filter Assembly

#### The return air inlet shall have a factory supplied primary removable, washable filter.

#### The unit shall be equipped with factory supplied secondary 3M Micro Dust Filter.

#### The filter access shall be from the front of the unit.

### Coil Assembly

#### Unit shall have a factory built coil comprised of aluminum fins mechanically bonded on copper tubing.

#### Unit shall have minimum of 2 rows of coils.

#### Unit shall have a factory supplied condensate drain pan below the coil.

#### Unit shall be designed for gravity drain.

#### Unit shall have a factory insulated drain hose to handle condensate.

#### Unit shall have provision of 45° flare refrigerant pipe connections.

#### The coil shall be factory pressure tested at a minimum of 626 psig.

#### All refrigerant piping from outdoor unit to indoor unit shall be field insulated.

### Microprocessor Control

#### The unit shall have a factory installed microprocessor controller capable of performing functions necessary to operate the system.

#### Systems are designed for and intended to operate with an LG proprietary controller to achieve full variable-speed performance and rated efficiencies.

#### The indoor unit shall be able to communicate with the outdoor unit using a field supplied minimum of 18 AWG, 2-conductor, stranded, shielded or unshielded communication cable.  If shielded, it must be grounded to chassis at ODU only.

#### Central control shall be available through a terminal connection on the outdoor unit.

#### Group control shall be available to allow multiple indoor units to operate from a single LG controller, or allow connection of more than one LG controller to an indoor unit.

#### The unit controls shall operate the indoor unit using one of the five operating modes:

##### Auto operation

##### Heating

##### Cooling

##### Dry

##### Fan only

### Electrical

#### The unit electrical power shall be 208-230/1/60 (V/Ph/Hz)

#### The unit shall be capable of operating within voltage limits of +/- 10% of the rated voltage.

### Controls

#### The indoor unit shall be supplied with a wireless handheld controller.

#### An optional LG wired controller shall be available as an additional accessory.

#### An optional dry contact shall be available as an additional accessory.

#### The indoor unit shall have built-in (factory installed) Wi-Fi to allow monitoring and control through a smart device with the LG Smart ThinQ© application.

#### The indoor unit shall have a factory installed R32 refrigerant leak detection sensor designed to communicate with mitigation devices and 3rd party alarms and transmit a system error code upon detection of a refrigerant leak or sensor failure/expiration.

#### An optional single-port shutoff valve shall be available as an additional accessory.  The shutoff valve shall be designed to integrate with and respond to a signal from a connected R32 refrigerant leak detection sensor, to close the refrigerant valve upon receiving a signal that a refrigerant leak has been detected, or that the sensor has incurred a failure or reached its 10-year expiration date.

### Warranty

#### Please refer to the respective outdoor unit for applicable warranty.