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Single Zone Heat Pump Indoor Unit (Cassette – 1way) <KNUFB181A>
0. Operating Conditions
The indoor unit shall be capable of the following ambient operating range.
Cooling: 57°F WB to 77°F WB
Heating: 59°F DB to 81°F DB
General
The unit shall be manufactured by LG.
Units shall be factory assembled, wired, piped, and run tested.
Unit shall be designed to be installed for indoor application.
Unit shall be designed to mount recessed in the ceiling and use a surface mounted grille with air inlet and outlet on the bottom of the unit.
Casing/Panel 
0. Unit case shall be manufactured using galvanized steel plate. 
The unit shall be provided with an off-white Acrylonitrile Butadiene Styrene (ABS) polymeric resin grille. 
The grille shall have a tapered trim edge, and a hinged, spring clip (screw-less) return air filter-grille door.
Unit shall be provided with metal ears designed to support the unit weight on four corners.
Ears shall have pre-punched holes designed to accept field-supplied all thread rod hangers.
Cabinet Assembly
0. The unit shall have one supply air outlets and one return air inlet.
The supply air outlet shall be through a single directional slot diffuser with oscillating motorized guide vane designed to change the airflow direction.
The grille shall have a discharge range of motion of 40° in an up/down direction with capabilities of locking the vanes.

Unit shall have factory installed motorized louver to provide flow of air in up and down direction for uniform airflow.
Unit shall have factory installed motorized guide vane to control the direction of flow of air from side to side.
Unit shall be equipped with factory installed temperature thermistors for 
Return air. 
Refrigerant entering coil.
Refrigerant leaving coil.
Unit shall have a built-in control panel to communicate with the outdoor unit.
Unit shall have the following functions as standard.
Self-diagnostic function 
Auto restart function
Auto changeover function
Dehumidifying function
Forced operation
Hot Start
Sleep mode
Fan Assembly
0. The unit shall have a single direct driven crossflow tangential Sirocco fan made of high strength ABS GP-2305 polymeric resin.
The fan motor is Brushless Digitally controlled (BLDC) with permanently lubricated and sealed ball bearings.
The fan/motor assembly shall be mounted on vibration attenuating rubber grommets.
The fan speed shall be controlled using a microprocessor based direct digitally controlled algorithm.
In cooling mode, the indoor fan shall have the following settings: Low, Med, High, Power Cool, and Auto.
In heating mode, the indoor fan shall have the following settings: Low, Med, High, Power Heat, and Auto.
The Auto fan setting shall adjust the fan speed to most effectively achieve the set-point.
Filter Assembly
The return air inlet shall have a factory supplied removable, washable filter.
The filter access shall be from of the unit without the need for tools.
Coil Assembly
0. Unit shall have a factory-built coil comprised of aluminum fins mechanically bonded on copper tubing.
Unit shall have a minimum two row coil, 20 fins per inch.
Unit shall have a factory supplied condensate drain pan below the coil.
The unit shall have an installed and wired condensate drain pump capable of providing minimum 27.5 inch lift from the bottom surface of the unit.
The drain pump shall have a safety switch to shut off the unit if condensate rises too high in the drain pan.
Unit shall have provision of 45° flare refrigerant pipe connections.
The coil shall be factory pressure tested at a minimum of 626 psig.
All refrigerant piping from outdoor unit to indoor unit shall be field insulated.
Microprocessor Control
0. The unit shall have a factory-installed microprocessor controller capable of performing functions necessary to operate the system.
Systems are designed for and intended to operate with an LG proprietary controller to achieve full variable-speed performance and rated efficiencies.
The indoor unit shall be able to communicate with the outdoor unit using a field supplied minimum of 18 AWG, 2-conductor, stranded, shielded or unshielded communication cable.  If shielded, it must be grounded to chassis at ODU only. 
0. The indoor unit shall be able to operate with the fan turned off during system cooling thermal off.
The indoor unit shall be able to operate with a continuous fan setting.
Central control shall be available through a terminal connection on the outdoor unit.
Group control shall be available to allow multiple indoor units to operate from a single LG controller or allow connection of more than one LG controller to an indoor unit.
The unit controls shall operate the indoor unit using one of the five operating modes:
Auto changeover
Heating
Cooling
Dry
Fan only
Electrical
0. The unit electrical power shall be 208-230/1/60 (V/Ph/Hz)
The unit shall be capable of operating within voltage limits of +/- 10% of the rated voltage.
Controls
0. The indoor unit shall be supplied with a wireless handheld controller. 
An optional LG wired controller shall be available as an additional accessory.
An optional dry contact shall be available as an additional accessory.
The indoor unit shall have built-in (factory installed) Wi-Fi to allow monitoring and control through a smart device with the LG Smart ThinQ© application. 
The indoor unit shall have a factory installed R32 refrigerant leak detection sensor designed to communicate with mitigation devices and 3rd party alarms and transmit a system error code upon detection of a refrigerant leak or sensor failure/expiration.
An optional single-port shutoff valve shall be available as an additional accessory.  The shutoff valve shall be designed to integrate with and respond to a signal from a connected R32 refrigerant leak detection sensor, to close the refrigerant valve upon receiving a signal that a refrigerant leak has been detected, or that the sensor has incurred a failure or reached its 10-year expiration date.  
Warranty 
0. Please refer to the respective outdoor unit for applicable warranty.
For continual product development, LG Electronics USA Inc. reserves the right to change specifications without notice.
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