	
	
	



Part 1. PRODUCT(S) – Outdoor Units (Single Zone Systems-Cassette/Console/Ducted/VAHU)
Single Zone Heat Pump Outdoor Unit (Cassette/Console/Mid-Static Duct/VAHU) <KUSXB091A><KUSXB121A><KUSXB181A><KUSXB241A><KUSXB301A><KUSXB361A><KUSXB421A><KUSXB481A><KUSXB601A>
0. Product Design
0. The Single zone HVAC system shall be a variable capacity, direct expansion (DX) heat pump system consisting of a single outdoor unit and single indoor unit.  The outdoor unit shall have a single inverter compressor.  The outdoor unit shall be connected to the indoor unit with piping and control wiring.
0. The LG heat pump system shall be an air-cooled system consisting of a single outdoor unit connected to a single indoor unit.
0. Single zone system requires the indoor unit to be piped with the outdoor unit to complete the refrigeration system.
0. The system is capable of changing mode within a maximum time of three (3) minutes to ensure indoor temperature can be properly maintained.
0. The heat pump system will be available in 208/230V, 60Hz, 1 phase.
0. Operating Conditions
0. The outdoor unit shall be capable of the following ambient operating range.
Cooling: 5°F DB to 118°F DB <with optional low ambient kit from -4°F DB to 118°F DB >
Heating: -4°F WB to 64°F WB
B. General
0. The unit shall be manufactured by LG.
The air-conditioning system shall use R32 refrigerant.
Each system shall have one air source outdoor unit.
The refrigerant circuit shall be field piped to a single matching indoor unit to control the heating or cooling operation of the system effectively and efficiently.
All refrigerant piping from outdoor unit to indoor unit shall be field insulated.
Factory installed microprocessor controls in the outdoor unit and indoor unit shall perform functions to efficiently operate the single zone system and communicate via minimum 18 AWG, 2-conductor, stranded, shielded or unshielded communication cable.  If shielded, it must be grounded to chassis at ODU only.
Systems are designed for and intended to operate with an LG proprietary controller to achieve full variable-speed performance and rated efficiencies.
Central control shall be available through a terminal connection on the outdoor unit.
The outdoor unit shall be internally assembled, wired, and piped from the factory.
The factory assembled system shall have the outdoor unit fitted with refrigerant strainer, check valves, oil separator, accumulator, 4-way reversing valve, electronic expansion valve, high side and low side refrigerant charging ports, and a service port.
C. Piping capabilities
0. The outdoor unit shall be capable of operating at an elevation of 49.2 feet <KUSXB091A><KUSXB121A> or 98.4 feet <KUSXB181A><KUSXB241A><KUSXB301A><KUSXB361A><KUSXB421A><KUSXB481A><KUSXB601A> above or below the indoor unit.
The outdoor unit shall be capable of operating with up to 66 feet <KUSXB091A><KUSXB121A>, 164 feet <KUSXB181A><KUSXB241A><KUSXB301A> or 246 feet <KUSXB361A><KUSXB421A><KUSXB481A><KUSXB601A> of total equivalent refrigerant piping length.
D. Defrost Operations
0. The outdoor unit shall be capable of auto defrost operation to melt accumulated ice off the outdoor unit heat exchanger. The defrost cycle control shall be based on outdoor ambient temperatures and outdoor unit heat exchanger temperatures.
0. The outdoor units shall accommodate an optional drain pan heater.
E. Oil Management
0. The outdoor unit shall have an oil injection mechanism to ensure a consistent film of oil on all moving compressor parts at low speed. 
The outdoor unit shall have an oil separator to separate oil mixed with the refrigerant gas during compression and return oil to the compressor.
F. Fan Assembly
0. Each 3/4-to-2.5-ton outdoor unit <KUSXB091A><KUSXB121A><KUSXB181A> <KUSXB241A><KUSXB301A> shall be equipped with one direct drive variable speed propeller fan with Brushless Digitally Controlled (BLDC) motor with a horizontal air discharge.
Each 3-to-5-ton outdoor unit <KUSXB361A><KUSXB421A><KUSXB481A><KUSXB601A>shall be equipped with two direct drive variable speed propeller fans with BLDC motors with a horizontal air discharge.
The fan blades shall be made of Acrylonitrile Butadiene Styrene (ABS) material.
The fan(s) shall be equipped with permanently lubricated bearings.
The fan motor(s) shall have variable speed to a maximum of 850 RPM <KUSXB091A><KUSXB121A>, or 760 RPM <KUSXB181A><KUSXB241A><KUSXB301A>, or 750 RPM <KUSXB361A><KUSXB421A><KUSXB481A><KUSXB601A>.
The fan(s) shall have a raised guard to help prevent contact with moving parts.
G. Cabinet
0. The outdoor unit cabinet shall be made of pre-coated metal (PCM).
The front/side panels of the outdoor unit shall be removable type for access to internal components.
The outdoor unit cabinet shall be tested in accordance with ASTM B-117 salt spray test procedure for a minimum of 1000 hours.
H. Outdoor Coil
0. The outdoor unit shall have a factory-built coil comprised of aluminum fins mechanically bonded to copper tubing.
The aluminum fins shall have factory applied corrosion resistant GoldFin™ material.
Coil coating shall be tested in accordance with ASTM B-117 salt spray test procedure for a minimum of 1000 hours.
The outdoor unit coil shall be factory tested to a pressure of 626 psig.
The coil for each outdoor unit shall have a minimum of 14 Fins per Inch (FPI).
The coil for each outdoor unit shall have a 2-row heat exchanger.
The outdoor unit cabinet shall have a coil guard.
I. Compressor
0. The outdoor <KUSXB091A><KUSXB121A><KUSXB181A><KUSXB241A> unit(s) shall be equipped with one hermetically sealed, digitally controlled, inverter driven twin-rotary compressor.
The outdoor <KUSXB301A><KUSXB361A><KUSXB421A><KUSXB481A><KUSXB601A> unit(s) shall be equipped with one hermetically sealed, digitally controlled, inverter driven R1 scroll compressor.
The inverter driven, digitally controlled compressor shall be capable of operating in a frequency range from 10 Hz to 90 Hz (cooling) and 10 Hz to 100 Hz (heating) <KUSXB091A><KUSXB121A><KUSXB301A>, with control in 1 Hz increments.
The inverter driven, digitally controlled compressor shall be capable of operating in a frequency range from 15 Hz to 80 Hz (cooling) and 15 Hz to 100 Hz (heating) <KUSXB181A><KUSXB241A>, with control in 1 Hz increments.
The inverter driven, digitally controlled compressor shall be capable of operating in a frequency range from 10 Hz to 120 Hz (cooling) and 10 Hz to 135 Hz (heating) <KUSXB361A><KUSXB421A><KUSXB481A>, with control in 1 Hz increments.
The inverter driven, digitally controlled compressor shall be capable of operating in a frequency range from 15 Hz to 110 Hz (cooling) and 15 Hz to 120 Hz (heating) <KUSXB601A>, with control in 1 Hz increments.
The compressor shall be mounted on vibration attenuating rubber grommets.
The compressor shall use a factory charge of Polyvinyl Ether (PVE) oil.
The compressor bearing(s) shall have Teflon™ coating.
The compressor shall be equipped with over-current protection. 
Fixed speed, non-inverter driven compressors shall not be permitted.
J. Sound Levels
0. The compressor(s) shall be wrapped with heat resistant foil faced, sound deadening blanket that covers all exposed surfaces of the compressor. Sound deadening blankets shall be secured in place by use of a Velcro™ tool-less joint sealing system with a minimum of ½” of overlap along all seams. The sound deadening compressor blanket shall be engineered to leave no direct sound path between the outer surface of the body of the compressor and the surrounding environment.
0. The outdoor unit shall have sound levels not exceeding 56 dB(A) tested in an anechoic chamber under ISO 3745 standard. 
0. A field setting shall be available to program the outdoor unit to reduce sound levels at night, when desired, to a selectable level while still able to meet building load requirements. This mode is available during cooling operation.
K. Sensors
0. The outdoor unit shall have 
Suction temperature sensor
Discharge temperature sensor
High pressure sensor
Low Pressure sensor
Outdoor ambient temperature sensor
Outdoor unit heat exchanger temperature sensor
L. Wind Load Installations for Outdoor Units
0. Provide Florida wind Load Installation Drawings that meet the requirements of the 2020 Florida Building Code, 7th Edition and ASCE Standard 7-2016 with submittal.
M. Warranty 
1. Limited Warranty Period
STANDARD FIVE (5) YEAR WARRANTY FOR A QUALIFIED SYSTEM - The Part(s) of a qualified System, including the compressor, are warranted for a period (the “Standard Parts Warranty Period”) ending five (5) years after the date of original installation. In the absence of proof of installation the warranty date will end five (5) years from the date of manufacture. 
ADDITIONAL TWO (2) YEAR COMPRESSOR PART WARRANTY - The Compressor is warranted for an additional two (2) year period after the end of the applicable Standard Part Warranty Period (the “Compressor Warranty Period”).
Extended Warranty
The Standard Warranty Period and the Compressor Warranty Period are extended to a total of ten (10) years (the “Extended Warranty Period”) for qualified Systems that have been (a) installed by a party that has completed the Training Requirements, (b) installation is pursuant to LG’s published instructions, and (c) product is registered within 60 days of startup at www.lg-dfs-warranty.com.
For continual product development, LG Electronics USA Inc. reserves the right to change specifications without notice.
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