Guide Specifications

# PRODUCT(S) - Indoor Units (Multi Zone Systems)

## Ceiling Cassette – 1 Way <KNMFB071A><KNUFB091A><KNUFB121A><KNUFB181A>

### Operating Conditions

#### The indoor unit shall be capable of the following ambient operating range.

##### Cooling: 57°F DB to 77°F WB

##### Heating: 59°F WB to 81°F DB

### General

#### Unit shall be manufactured by LG.

#### Unit shall be factory assembled, wired, piped and run tested.

#### Unit shall be designed to be installed for indoor application.

#### Unit shall be designed to mount recessed in the ceiling and use a surface mounted grille with air inlet and outlet on the bottom of the unit

### Casing/Panel

#### Unit case shall be manufactured using galvanized steel plate.

#### The unit shall be provided with an off-white Acrylonitrile Butadiene Styrene (ABS) polymeric resin grille.

#### The grille shall have a tapered trim edge, and a hinged, spring clip (screw-less) return air filter-grille door.

#### Unit shall be provided with metal ears designed to support the unit weight on four corners.

#### Ears shall have pre-punched holes designed to accept field supplied all thread rod hangers.

### Cabinet Assembly

#### Unit shall have one supply air outlet and one return air inlet.

#### The supply air outlet shall be through a single directional slot diffuser with oscillating motorized guide vane designed to adjust the airflow direction.

#### The grille shall have a discharge range of motion of 40° in an up/down direction with capabilities of locking the vanes.

#### Unit shall have factory installed motorized louver to provide flow of air in up and down direction for uniform airflow.

#### Unit shall have factory installed motorized guide vane to control the direction of flow of air from side to side.

#### Unit shall be equipped with factory installed temperature thermistors for

##### Return air

##### Refrigerant entering coil

##### Refrigerant leaving coil

#### Unit shall have a built-in control panel to communicate with the outdoor unit.

#### Unit shall have the following functions as standard

##### Self-diagnostic function

##### Auto restart function

##### Auto operation function

##### Dehumidifying function

##### Forced operation

##### Hot Start

##### Sleep mode

### Fan Assembly

#### The unit shall have a single direct driven crossflow tangential Sirocco fan made of high strength ABS GP-2305 polymeric resin.

#### The fan motor is Brushless Digitally controlled (BLDC) with permanently lubricated and sealed ball bearings.

#### The fan/motor assembly shall be mounted on vibration attenuating rubber grommets.

#### The fan speed shall be controlled using microprocessor based direct digitally controlled algorithm.

#### In cooling mode, the indoor fan shall have the following settings: Low, Med, High, Power Cool, and Auto.

#### In heating mode, the indoor fan shall have the following settings: Low, Med, High, Power Heat, and Auto.

#### The Auto fan setting shall adjust the fan speed to most effectively achieve the set-point.

### Filter Assembly

#### The return air inlet shall have a factory supplied removable, washable filter.

#### The filter access shall be from the bottom of the unit without the need for tools.

### Coil Assembly

#### Unit shall have a factory-built coil comprised of aluminum fins mechanically bonded on copper tubing.

#### Unit shall have a minimum two row coil, 20 fins per inch.

#### Unit shall have a factory supplied condensate drain pan below the coil.

#### Unit shall have an installed and wired condensate drain pump capable of providing minimum 27.5 inch lift from bottom surface of the unit.

#### The drain pump shall have a safety switch to shut off the unit if condensate rises to high in the drain pan.

#### Unit shall have provision of 45° flare refrigerant pipe connections.

#### The coil shall be factory pressure tested at a minimum of 626 psig.

#### All refrigerant piping from outdoor unit to indoor unit shall be field insulated.

### Microprocessor Control

#### The unit shall have a factory installed microprocessor controller capable of performing functions necessary to operate the system.

#### Systems are designed for and intended to operate with an LG proprietary controller to achieve full variable-speed performance and rated efficiencies.

#### The indoor unit shall be able to communicate with the outdoor unit using a field supplied minimum of 18 AWG, 2-conductor, stranded, shielded or unshielded communication cable.  If shielded, it must be grounded to chassis at ODU only.

#### Central control shall be available through a terminal connection on the outdoor unit.

#### Group control shall be available to allow multiple indoor units to operate from a single LG controller, or allow connection of more than one LG controller to an indoor unit.

#### The unit controls shall operate the indoor unit using one of the five operating modes:

##### Auto operation

##### Heating

##### Cooling

##### Dry

##### Fan only

### Electrical

#### The unit electrical power shall be 208-230/1/60 (V/Ph/Hz)

#### The unit shall be capable of operating within voltage limits of +/- 10% of the rated voltage.

### Controls

#### The indoor unit shall be supplied with a wireless handheld controller.

#### An optional LG wired controller shall be available as an additional accessory.

#### An optional dry contact shall be available as an additional accessory.

#### The indoor unit shall have built-in (factory installed) Wi-Fi to allow monitoring and control through a smart device with the LG Smart ThinQ© application.

#### The indoor unit shall have a factory installed R32 refrigerant leak detection sensor designed to communicate with mitigation devices and 3rd party alarms and transmit a system error code upon detection of a refrigerant leak or sensor failure/expiration.

#### An optional single-port shutoff valve shall be available as an additional accessory.  The shutoff valve shall be designed to integrate with and respond to a signal from a connected R32 refrigerant leak detection sensor, to close the refrigerant valve upon receiving a signal that a refrigerant leak has been detected, or that the sensor has incurred a failure or reached its 10-year expiration date.

### Warranty

#### Please refer to the respective outdoor unit for applicable warranty.