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Part 1. PRODUCT(S) - Indoor Units (Multi Zone Systems)
Ducted – Mid Static <KNUJB301A><KNUJB361A>
0. Operating Conditions
The indoor unit shall be capable of the following ambient operating range.
Cooling: 57°F DB to 77°F WB
Heating: 59°F WB to 81°F DB
General
0. Unit shall be manufactured by LG.
Unit shall be factory assembled, wired, piped and run tested.
Unit shall be designed to be installed for indoor application.
Unit shall be designed to mount fully concealed above the finished ceiling.
Unit shall have opening to supply air from front horizontal and a dedicated rear horizontal return.
The supply air opening shall be flanged for field installed ductwork that shall not exceed the external static pressure limitation of the unit.
Casing/Panel 
0. Unit case shall be manufactured using galvanized steel plate.
The cold surfaces of the unit shall be covered internally with a coated polystyrene insulating material.
Unit shall be provided with hanger brackets designed to support the unit weight on four corners.
Hanger brackets shall have pre-punched holes designed to accept field supplied, all thread rod hangers.
Cabinet Assembly
0. Unit shall have supply air discharge outlets horizontal and a return air inlet horizontal.
Unit shall be equipped with factory installed temperature thermistors for 
Return air 
Refrigerant entering coil
Refrigerant leaving coil
Unit shall have a built-in control panel to communicate with the outdoor unit.
Unit shall have the following functions as standard
Self-diagnostic function 
Auto restart function
Auto operation function
Dehumidifying function 
Child lock function
Dual thermistor control
Hot Start
Sleep mode
External static pressure (ESP) control
Fan Assembly
0. The unit shall have two direct driven Sirocco fans. 
The fans shall be made of high strength ABS GP-2200 polymeric resin.
The fans shall be mounted on a common shaft. 
The fan motor shall be Brushless Digitally controlled (BLDC) with permanently lubricated and sealed ball bearings.
The fan/motor assembly shall be mounted on vibration attenuating rubber grommets.
The fan speed shall be controlled using microprocessor based direct digitally controlled algorithm.
In cooling mode, the indoor fan shall have the following settings: Low, Med, High, and Auto.
In heating mode, the indoor fan shall have the following settings: Low, Med, High, and Auto.
The Auto fan setting shall adjust the fan speed to most effectively achieve the set-point.
Each of the settings can be field adjusted from the factory setting (RPM/ESP).
Unit shall be designed for high speed air volume against an external static pressure of up to 0.59 inches water gauge.
Filter Assembly
0. The return air inlet shall have a factory supplied removable, washable filter.
The filter access shall be from the rear of the unit.
<Optional Return filter box with high-efficiency filter shall be field provided and installed not to exceed external static pressure limitation of the high static ducted indoor unit.>
<The unit shall have provision to mate directly with high efficiency filter box to accommodate 1” or 2”thick field provided MERV rated filter.>
Coil Assembly
0. Unit shall have a factory built coil comprised of aluminum fins mechanically bonded on copper tubing.
Unit shall have minimum of 3 rows of coils.
Unit shall have a factory supplied condensate drain pan below the coil constructed of HIPS (high impact polystyrene resin).
Unit shall have an installed and wired condensate drain pump capable of providing minimum 27.5 inch lift from bottom surface of the unit.
The drain pump shall have a safety switch to shut off the unit if condensate rises too high in the drain pan.
Unit shall have provision of 45° flare refrigerant pipe connections.
The coil shall be factory pressure tested at a minimum of 626 psig.
All refrigerant piping from outdoor unit to indoor unit shall be field insulated.
Microprocessor Control
0. The unit shall have a factory installed microprocessor controller capable of performing functions necessary to operate the system.
Systems are designed for and intended to operate with an LG proprietary controller to achieve full variable-speed performance and rated efficiencies.
The indoor unit shall be able to communicate with the outdoor unit using a field supplied minimum of 18 AWG, 2-conductor, stranded, shielded or unshielded communication cable.  If shielded, it must be grounded to chassis at ODU only.
Central control shall be available through a terminal connection on the outdoor unit.
Group control shall be available to allow multiple indoor units to operate from a single LG controller, or allow connection of more than one LG controller to an indoor unit.
The unit controls shall operate the indoor unit using one of the five operating modes:
Auto operation
Heating
Cooling
Dry
Fan only
Electrical
0. The unit electrical power shall be 208-230/1/60 (V/Ph/Hz)
The unit shall be capable of operating within voltage limits of +/- 10% of the rated voltage.
Controls
0. The indoor unit shall use controls provided by the manufacturer c/o separately purchased and installed LG wired controller to perform all functions necessary to operate the system effectively and efficiently.
0. An optional wireless handheld controller shall be available as an additional accessory for use with installed LG wired controller.
0. An optional dry contact shall be available as an additional accessory.
0. The indoor unit shall accommodate an optional Wi-Fi module as an additional accessory to allow monitoring and control through a smart device with the LG Smart ThinQ© application.
0. The indoor unit shall have a factory installed R32 refrigerant leak detection sensor designed to communicate with mitigation devices and 3rd party alarms and transmit a system error code upon detection of a refrigerant leak or sensor failure/expiration.
0. An optional single-port shutoff valve shall be available as an additional accessory.  The shutoff valve shall be designed to integrate with and respond to a signal from a connected R32 refrigerant leak detection sensor, to close the refrigerant valve upon receiving a signal that a refrigerant leak has been detected, or that the sensor has incurred a failure or reached its 10-year expiration date.
Warranty 
0. Please refer to the respective outdoor unit for applicable warranty.
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