Guide Specifications

# PRODUCT(S) - Indoor Units (Multi Zone Systems)

## Ducted – Multi-Position Air Handling Unit <KNMLB121A><KNMLB181A><KNMLB241A><KNMLB301A><KNMLB361A>

### Operating Conditions

#### The indoor unit shall be capable of the following ambient operating range.

##### Cooling: 57°F DB to 77°F WB

##### Heating: 59°F WB to 81°F DB

### General

#### Unit shall be manufactured by LG.

#### Unit shall be factory assembled, wired, piped and run tested.

#### Unit shall be designed to be installed for indoor application.

#### Unit shall be designed to mount fully concealed behind the wall or above the finished ceiling.

#### The unit case shall be designed to accept an internal, optional LG electric strip heater mounted in the reheat position, available in 3, 5, 8kW <KNMLB121A>, 3, 5, 8, 10 kW <KNMLB181A><KNMLB241A><KNMLB301A>, and 3, 5, 8, 10, 15 kW <KNMLB361A> for field installation per installation instructions.

#### The supply air opening shall be flanged for field installed ductwork that shall not exceed the external static pressure limitation of the unit.

### Casing/Panel

#### Unit case shall be manufactured using 22-gauge Pre Coated Metal (PCM).

#### The external surface shall be finished with a high gloss baked enamel finish.

#### The finish color shall be morning fog.

#### The cold surfaces of the unit shall be internally insulated with ½” foil faced polystyrene fiber insulation.

#### The inside surface of fan assembly door access panel shall be treated with ½” polystyrene fiber insulation, encapsulated on both sides.

#### The access panel shall be sealed along the edges with reinforced foil faced covering to prevent deterioration caused by panel removal.

#### All access panels shall be provided with gasket seals to minimize air leakage.

### Cabinet Assembly

#### The unit shall be designed to operate in the vertical (up flow and down flow) configuration and horizontal (left and right) end discharge. Down flow configuration shall require an optional downflow conversion kit.

##### Unit shall, in the vertical position, have opening for supply air from top (or bottom) with a dedicated bottom (or top) vertical return and in the horizontal position supply air shall be from the left (or right) end with the return air from the right (or left) end.

#### Unit shall be equipped with factory installed temperature thermistors for

##### Return air

##### Refrigerant entering coil

#### Refrigerant leaving coil

#### Unit shall have a built-in control panel to communicate with the outdoor unit.

#### Unit shall have the following functions as standard

##### Self-diagnostic function

##### Auto restart function

##### Auto operation function

##### Dehumidifying function

##### Child lock function

##### Dual thermistor control

##### Hot Start

##### Sleep mode

##### External static pressure (ESP) control

### Fan Assembly

#### The unit shall have an integral fan assembly consisting of galvanized steel housing and forward curve fan wheel.

#### The fan motor shall be Electronically Commutated Motor (ECM) <KNMLB121A><KNMLB181A><KNMLB241A> (at launch), <KNMLB301A><KNMLB361A> (starting 7/1/2025) with permanently lubricated and sealed ball bearings.

#### The fan/motor assembly shall be mounted on vibration attenuating rubber grommets.

#### The fan speed shall be controlled using microprocessor based direct digitally controlled algorithm.

#### In cooling mode, the indoor fan shall have the following settings: Low, Med, High, and Auto.

#### In heating mode, the indoor fan shall have the following settings: Low, Med, High, and Auto.

#### The Auto fan setting shall adjust the fan speed to most effectively achieve the set-point.

#### The ECM fan shall adjust and deliver constant airflow regardless of permitted external static pressure.

#### The unit shall be designed for high-speed air volume against an external static pressure from 0.1” to 1.0” water gauge.

### Filter Assembly

#### The unit shall be supplied with a filter rack capable of accepting a field supplied 16” x 20” x 1” filter cartridge <KNMLB121A><KNMLB181A><KNMLB241A>, and a filter rack capable of accepting a field supplied 20” x 20” x 1” filter cartridge <KNMLB301A><KNMLB361A>.

#### The filter rack shall be equipped with guides to keep filter centered in the rack.

#### The filter access shall be from the front of the unit without removing coil or fan area access panel.

#### The filter access door shall be fitted with thumb screws that can be removed without the use of any tool.

### Coil Assembly

#### Unit shall have a factory built coil comprised of aluminum fins mechanically bonded on copper tubing.

#### Unit shall have minimum of 2 rows of coils.

#### Unit shall have a factory supplied condensate drain pan below the coil constructed of HIPS (high impact polystyrene resin).

#### The drain pan shall be designed for gravity drain.

#### Unit shall have provision of 45° flare refrigerant pipe connections.

#### The coil shall be factory pressure tested at a minimum of 626 psig.

#### All refrigerant piping from outdoor unit to indoor unit shall be field insulated.

### Microprocessor Control

#### The unit shall have a factory installed microprocessor controller capable of performing functions necessary to operate the system.

#### Systems are designed for and intended to operate with an LG proprietary controller to achieve full variable-speed performance and rated efficiencies.

#### The indoor unit shall be able to communicate with the outdoor unit using a field supplied minimum of 18 AWG, 2-conductor, stranded, shielded or unshielded communication cable.  If shielded, it must be grounded to chassis at ODU only.

#### Central control shall be available through a terminal connection on the outdoor unit.

#### Group control shall be available to allow multiple indoor units to operate from a single LG controller, or allow connection of more than one LG controller to an indoor unit.

#### The unit controls shall operate the indoor unit using one of the five operating modes:

##### Auto operation

##### Heating

##### Cooling

##### Dry

##### Fan only

#### The unit shall have provision for W-2 terminal connection for second stage heat.

#### The unit shall be able to operate in either cooling or heating mode for testing and/or commissioning.

#### The indoor unit shall be able to operate with the fan turned off during system cooling thermal off.

#### The indoor unit shall be able to operate with a continuous fan setting.

#### The unit shall have adjustable, multi-step cooling and heating mode thermal on/off temperature range settings.

#### The system shall include a product check function to access and display indoor unit type and capacity from a wired programmable zone controller.

### Electrical

#### The unit electrical power shall be 208-230/1/60 (V/Ph/Hz)

#### The unit shall be capable of operating within voltage limits of +/- 10% of the rated voltage.

### Controls

#### The indoor unit shall use controls provided by the manufacturer c/o separately purchased and installed LG wired controller to perform all functions necessary to operate the system effectively and efficiently.

#### An optional wireless handheld controller shall be available as an additional accessory for use with installed LG wired controller.

#### An optional dry contact shall be available as an additional accessory.

#### The indoor unit shall accommodate an optional Wi-Fi module as an additional accessory to allow monitoring and control through a smart device with the LG Smart ThinQ© application.

#### The indoor unit shall have a factory installed R32 refrigerant leak detection sensor designed to communicate with mitigation devices and 3rd party alarms and transmit a system error code upon detection of a refrigerant leak or sensor failure/expiration.

#### An optional single-port shutoff valve shall be available as an additional accessory.  The shutoff valve shall be designed to integrate with and respond to a signal from a connected R32 refrigerant leak detection sensor, to close the refrigerant valve upon receiving a signal that a refrigerant leak has been detected, or that the sensor has incurred a failure or reached its 10-year expiration date.

### Warranty

#### Please refer to the respective outdoor unit for applicable warranty.