Guide Specifications

## Single Zone with LGRED° Heat Pump Indoor Unit (Cassette – 4way) <KNUDB181A><KNSCB241A><KNSCB301A><KNSCB361A>KNSCB421A><KNSCB481A>

### Operating Conditions

#### The indoor unit shall be capable of the following ambient operating range.

##### Cooling: 57°F WB to 77°F WB

##### Heating: 59°F DB to 81°F DB

### General

#### The unit shall be manufactured by LG.

#### Unit shall be factory assembled, wired, piped, and run tested.

#### Unit shall be designed to be installed for indoor application.

#### Unit shall be designed to mount recessed in the ceiling and has a surface mounted concentric grille on the bottom of the unit.

#### The indoor units have sound ratings no higher than 56 dB(A) as tested per ISO Standard 3745.

#### The unit <KNUDB181A> shall be compatible with both standard single zone and LGRED° outdoor units in addition to Multi Zone outdoor units.

#### The unit <KNSCB241A~KNSCB481A> shall only be compatible with standard single zone standard and LGRED° outdoor units.

#### The unit <KNUDB181A> shall be available in a 2’ x 2’ chassis.

#### The unit <KNSCB241A><KNSCB301A><KNSCB361A><KNSCB421A><KNSCB481A> shall be available in a 3’ x 3’ chassis.

### Casing/Panel

#### Unit case shall be manufactured using galvanized steel plate.

#### The unit shall be provided with an off-white Acrylonitrile Butadiene Styrene (ABS) polymeric resin architectural grille.  <An optional small profile matte finish grille shall be available as an additional accessory>

#### The grille shall have a tapered trim edge, and a hinged, spring clip (screw-less) return air filter-grille door.

#### Unit shall be provided with metal ears designed to support the unit weight on four corners.

#### Ears shall have pre-punched holes designed to accept field supplied all thread rod hangers.

### Cabinet Assembly

#### The unit shall have four supply air outlets and one return air inlet.

#### The 3’ x 3’ unit <KNSCB241A~KNSCB481A> shall be equipped with dual vane capable of providing optimized angle for supply air to move air dynamically in all directions.

#### The supply air outlet shall be through four-directional slot diffusers each equipped with independent oscillating motorized guide vane designed to change the airflow direction.

#### The panel vanes shall have a discharge range of motion of 10° - 85° in an up/down direction with capabilities of locking the vanes.

#### The unit shall have independent vane operation using separate step motors and be capable of controlling all four vanes independently.

#### The unit shall have a guide vane algorithm designed to sequentially change the predominant discharge airflow direction in counterclockwise pattern.

#### Guide vanes shall provide airflow in all directions.

#### Unit shall be equipped with factory installed humidity sensor <KNSCB241A~KNSCB481A> as well as temperature thermistors for

##### Return air

##### Refrigerant entering coil

##### Refrigerant leaving coil

#### Unit shall have a built-in control panel to communicate with the outdoor unit.

#### The unit shall have provision for fresh air ventilation through a knock-out on the cabinet.

#### The <KNUDB181A> unit shall have factory designated branch duct knockouts on the unit case.

##### The branch duct knockouts shall have the ability to duct up to half of the unit airflow capacity.

##### The branch duct shall be ducted within the same room as the indoor unit.

#### Unit shall have the following functions as standard.

##### Self-diagnostic function

##### Auto restart function

##### Auto changeover function

##### Floor Temperature sensor

##### Human detection sensor

##### Dehumidifying function

##### Forced operation

##### Hot Start

##### Sleep mode

### Fan Assembly

#### The unit shall have a single direct driven turbo fan.

#### The fan shall be made of high strength ABS HT-700 polymeric resin.

#### The fan motor is Brushless Digitally controlled (BLDC) with permanently lubricated and sealed ball bearings.

#### The fan/motor assembly shall be mounted on vibration attenuating rubber grommets.

#### The fan speed shall be controlled using a microprocessor based direct digitally controlled algorithm.

#### In cooling mode, the indoor fan shall have the following settings: Low, Med, High, Power Cool, and Auto.

#### In heating mode, the indoor fan shall have the following settings: Low, Med, High, and Auto <KNUDB181A><KNSCB241A~KNSCB481A> and Power Heat <KNSCB241A~KNSCB481A>.

#### The Auto fan setting shall adjust the fan speed to achieve the set-point most effectively.

#### Unit shall have factory installed motorized louvers to provide flow of air in up and down direction for uniform airflow.

### Filter Assembly

#### The return air inlet shall have a factory supplied 14” x 14” x 1” <KNUDB181A> or 20.5” x 20.5” x 1” <KNSCB241A~KNSCB481A> primary removable, washable filter.

#### The filter access shall be from the bottom of the unit.

### Coil Assembly

#### Unit shall have a factory-built coil comprised of aluminum fins mechanically bonded on copper tubing.

#### Unit <KNUDB181A><KNSCB241A> shall have minimum of 2 rows of coils. Unit <KNSCB301A><KNSCB361A><KNSCB421A><KNSCB481A> shall have 3 rows of coils.

#### Unit shall have a factory supplied condensate drain pan below the coil.

#### The unit shall have an installed and wired condensate drain pump capable of providing minimum 27.5 inch lift <KNUDB181A> or 31.5 inch lift <KNSCB241A~KNSCB481A> from the bottom surface of the unit.

#### The drain pump shall have a safety switch to shut off the unit if condensate rises too high in the drain pan.

#### Unit shall have provision of 45° flare refrigerant pipe connections.

#### The coil shall be factory pressure tested at a minimum of  626 psig.

#### All refrigerant piping from outdoor unit to indoor unit shall be field insulated.

### Microprocessor Control

#### The unit shall have a factory installed microprocessor controller capable of performing functions necessary to operate the system.

#### Systems are designed for and intended to operate with an LG proprietary controller to achieve full variable-speed performance and rated efficiencies.

#### The indoor unit shall be able to communicate with the outdoor unit using a field supplied minimum of 18 AWG, 2-conductor, stranded, shielded or unshielded communication cable.  If shielded, it must be grounded to chassis at ODU only.

#### Central control shall be available through a terminal connection on the outdoor unit.

#### Group control shall be available to allow multiple indoor units to operate from a single LG controller or allow connection of more than one LG controller to an indoor unit.

#### The indoor unit shall be able to operate with the fan turned off during system cooling thermal off.

#### The indoor unit shall be able to operate with a continuous fan setting.

#### The unit controls shall operate the indoor unit using one of the five operating modes:

##### Auto changeover

##### Heating

##### Cooling

##### Dry

##### Fan only

### Electrical

#### The unit electrical power shall be 208-230/1/60 (V/Ph/Hz)

#### The unit shall be capable of operating within voltage limits of +/- 10% of the rated voltage.

### Controls

#### The indoor unit shall be supplied with a wireless handheld controller.

#### An optional LG wired controller shall be available as an additional accessory.

#### An optional dry contact shall be available as an additional accessory.

#### The indoor unit shall accommodate an optional Wi-Fi module as an additional accessory to allow monitoring and control through a smart device with the LG Smart ThinQ© application.

#### The indoor unit shall have a factory installed R32 refrigerant leak detection sensor designed to communicate with mitigation devices and 3rd party alarms and transmit a system error code upon detection of a refrigerant leak or sensor failure/expiration.

#### An optional single-port shutoff valve shall be available as an additional accessory.  The shutoff valve shall be designed to integrate with and respond to a signal from a connected R32 refrigerant leak detection sensor, to close the refrigerant valve upon receiving a signal that a refrigerant leak has been detected, or that the sensor has incurred a failure or reached its 10-year expiration date.

### Warranty

#### Please refer to the respective outdoor unit for applicable warranty.