## Slide 1
LG HVAC Training
LG HVAC Training
Copyright ⓒ LG Electronics. all right reserved.

## Slide 2
Multi V DOAS
Trouble Shooting

## Slide 3
1. Introduction
1.0 Location of Key Parts
1.1 Location of Control Parts
1.2 Wiring Diagram
2. Trouble Shooting
2.1 Error Code Display
2.2 Error Code Table
2.3 Trouble Shooting
Contents
Insulation is attached to the outside of the product from the production on May.’22
Conventional (before May.’22)

## Slide 4
Introduction

## Slide 5
1. Introduction
1.1 Location of Key Parts
Main Coil
Hot Gas Reheat Coil
EC motor
3D Plug Fan
Heat Recovery Unit
Control Box
-Web UI,
-BACnet IP, Modbus RTU
Bottom Access Panel
(Fan Motor Assembly)
Filters (2”, MERV 8)
Gravity Drain
Drain Pump
Bottom Access Panel (Filter maintenance)
ARND153DCR4, ARND203DCR4
1 inch Insulation
Notes:  | System Layout

## Slide 6
1.2 Location of Control Parts
1. Introduction
BOTTOM PANEL
TOP PANEL
2
3
4
5
1
10
11
12
7
8
9
6
No | Description
1 | CAREL® Controller
2 | Main Module
3 | Main Coil EEV Module
4 | Reheat Coil EEV Module
5 | NTC Module
6 | UI Module
7 | HR Unit PCB
8 | SMPS
9 | Transformer
10 | RS485 1
11 | RS485 2
12 | Relay 1
Notes:  | System Layout

## Slide 7
1. Introduction
1.3 Wiring Diagram
No | Description
1 | CAREL® Controller
2 | Main Module
3 | Main Coil EEV Module
4 | Reheat Coil EEV Module
5 | NTC Module
6 | UI Module
7 | HR Unit PCB
8 | SMPS
9 | Transformer
10 | RS485 1
11 | RS485 2
12 | Relay 1
1
2
3
4
5
6
7
8
9
10
11
12
Notes:  | System Layout

## Slide 8
Trouble Shooting

## Slide 9
2. Troubleshooting
2.1 Error Code Display
• There are two levels of error code response.
(1) Level 1 : Immediate system shutdown
(2) Level 2 : Notify and keep operation
Error Indicator
Error Code Display
• Error codes are consist of 5 digits numbers. (Main module display right 4 digits only.)
[ Main Module ]
[ Carel Controller ]
[ Web UI ]
1
Error code
0 0 0
0
Error occurrence location
Fixed as 1
Error Occurrence Location
1 : DOAS system
2 : EEV Module
6 : ODU
7 : Supply Fan
8 : Exhaust Fan
9 : ERW
1
Error code
2
EEV module
Fixed as 1
0
0 0
EEV module location
EEV Module Location
1 : Main Coil
2 : Reheat Coil
3 : Recovery Coil
4 : Main Coil_2
• In case of EEV error (Second digit = 2),
Notes:  | System Layout

## Slide 10
2. Troubleshooting
2.2 Error Code Table
Category | Error Code | Level | Description | Details
Setting | 10001 | 1 | Need Product Setting | Product setting from Carel controller has not been set. Main module needs product information.
Forced Stop | 11001 | 1 | Forced Stop signal detection | When forced stop signal is detected for more than 3 seconds.
Drain Pump | 11002 | 1 | Float Switch or Drain Pump malfunction | Float Switch alarm is detected for more than 5 minutes.
Damper | 11003 | - | Reserved | Reserved
 | 11004 | - | Reserved | Reserved
 | 11005 | - | Reserved | Reserved
Filter | 11006 | 2 | Filter Alarm *if installed 3rd party Filter switch. | Differential pressure switch alarm for filter is detected.
 | 11007 | - | Reserved | Reserved
Communication | 11011 | 1 | Communication error with ODU (CEN A/B) | Central controller comm. Port (CEN A/B) of the ODU doesn’t respond for more than 3 minutes.
 | 11012 | 1 | ODU mismatch error | ODU is not compatible with DOAS system. (ODU main SW needs to be updated)
 | 11013 | 1 | Communication error with UI Module | Module doesn’t respond for more than 3 minutes.
 | 11014 | 1 | Communication error with NTC Module | Module doesn’t respond for more than 3 minutes.
 | 11015 | 1 | Communication error with fan communication board | Board doesn’t respond for more than 3 minutes.
 | 11021 | 1 | Communication error with EEV Module #1 (Main#1) | Module doesn’t respond for more than 3 minutes.
 | 11022 | 1 | Communication error with EEV Module #2 (Reheat) | Module doesn’t respond for more than 3 minutes.
 | 11023 | - | Reserved | Reserved
 | 11024 | - | Reserved | Reserved
Sensor | 11112 | 2 | OA Humidity sensor abnormal condition (UI #2) | Input voltage is less than 0.1V or more than 9.9V (for 3 minutes). - DOAS uses ODU humidity value as an alternative.
 | 11113 | 2 | SA Temperature sensor abnormal condition (UI #3) | Input voltage is less than 0.1V or more than 9.9V (for 3 minutes). - DOAS uses SA NTC sensor (RI#7) value as an alternative.
 | 11114 | 2 | SA Humidity sensor abnormal condition (UI #4) | Input voltage is less than 0.1V or more than 9.9V (for 3 minutes).
 | 11115 | 2 | SA differential pressure sensor abnormal condition (UI #5) | Input voltage is less than 0.1V or more than 9.9V (for 3 minutes).
 | 11116 | - | Reserved | Reserved
 | 11118 | 2 | CO2 sensor abnormal condition (UI #8) | Input voltage is less than 0.1V or more than 9.9V (for 3 minutes).
 | 11123 | 2 | Space Temp. sensor abnormal condition(UI #13) | Input voltage is less than 0.1V or more than 9.9V (for 3 minutes).
 | 11124 | 2 | Space Humid. sensor abnormal condition(UI #14) | Input voltage is less than 0.1V or more than 9.9V (for 3 minutes).
Notes:  | System Layout

## Slide 11
Category | Error Code | Level | Description | Details
Sensor | 11131 | 2 | Space Temp. sensor abnormal condition(RI #1) | Input value is too low or too high (component open or short).
 | 11133 | 2 | OA Temp. sensor abnormal condition (RI #3) | Input value is too low or too high (component open or short). - DOAS uses ODU temperature sensor value as an alternative.
 | 11134 | 2 | LAT #1 Temp. sensor abnormal condition (RI #4) | Input value is too low or too high (component open or short). - DOAS uses LAT #2 value as an alternative.
 | 11135 | 2 | LAT #2 Temp. sensor abnormal condition (RI #5) | Input value is too low or too high (component open or short). - DOAS uses LAT #1 value as an alternative.
 | 11136 | - | Reserved | Reserved
 | 11137 | 2 | SA Temp. sensor abnormal condition (RI #7) | Input value is too low or too high (component open or short). - DOAS uses LAT (Leaving Air Temp.) value as an alternative.
 | 11138 | 2 | Mix Temp. sensor abnormal condition (RI #8) | Input value is too low or too high (component open or short).
EEV Module #1 (Main Coil #1) | 12102 | 1 | Pipe-In Temp. sensor abnormal condition on EEV Module #1 (Main #1) | Input value is too low or too high (component open or short).
 | 12105 | 1 | Communication error between EEV Module#1 (Main #1) and ODU | Communication with ODU is not performing properly.
 | 12106 | 1 | Pipe-Out Temp. sensor abnormal condition on EEV Module #1 (Main #1) | Input value is too low or too high (component open or short).
EEV Module #2 (Reheat Coil) | 12202 | 2 | Pipe-In Temp. sensor abnormal condition on EEV Module #2 (Reheat) | Input value is too low or too high (component open or short).
 | 12205 | 2 | Communication error between EEV Module#2 (Reheat) and ODU | Communication with ODU is not performing properly.
 | 12206 | 2 | Pipe-Out Temp. sensor abnormal condition on EEV Module #2 (Reheat) | Input value is too low or too high (component open or short).
ODU | 16xxx | 1 | Error occurrence on ODU | Display ODU error codes by using right 3 digit * Refer to the ODU SVC manual for detail information.
SA fan driver | 17021 | 1 | [EC Motor] IPM HW Fault | IPM HW Fault
 | 17023 | 1 | [EC Motor] DC Link Voltage abnormal | DC Link voltage is too low or too high
 | 17026 | 1 | [EC Motor] Missing cable connection | Motor internal cable is disconnected
 | 17029 | 1 | [EC Motor] IPM over current | Motor driving current is too high
 | 17040 | 1 | [EC Motor] IPM current detection parts abnormal | Bad component on current detection
 | 17052 | 1 | [EC Motor] Communication error | Fan communication PCBA doesn’t receive response form the EC Motor for 30 seconds
 | 17057 | 1 | [EC Motor] Communication error | EC Motor doesn’t receive command for more than 3 minutes.
 | 17062 | 1 | [EC Motor] IPM Heatsink Temp abnormal | Heatsink Temp is over the spec
 | 17067 | 1 | [EC Motor] Motor Lock | Fan Motor is locked
2. Troubleshooting
2.2 Error Code Table
Notes:  | System Layout

## Slide 12
2. Troubleshooting
2.3 Trouble Shooting
Error No. 10001
• Symptom : System shutdown with displaying error code 0001 on the main module SSD. (10001 on the Carel controller or Web UI)
• Cause : When the new Carel controller is replaced as a service activity and it need the product information.
• Trouble shooting : Conduct initial product setting.
1. Push the Enter button at the model setting screen.
2. Search installed model No. using up and down button
3. Push the enter button
4. Check the model No. and model type
If you set wrong model No you can change it with below sequence
Menu  Ctrl. Variable  Advanced  Login  Set Password “7600” and push Enter Button.
Then Go to Menu again  Settings  DOAS Model Setting  and set the correct model name.
Notes:  | System Layout

## Slide 13
2. Troubleshooting
2.3 Trouble Shooting
Error No. 11001
• Symptom : System shutdown with displaying code 1001 on the main module SSD. (11001 on the Carel controller or Web UI)
• Cause : The forced stop input is opened.
• Trouble shooting : Conduct initial product setting.
1. Check the 12V and DCOM is shorted.
2. Check the forced stop input is opened. - The input signal from forced stop device should be normal closed type and dry contact output.
Short
Forced Stop Input
DI1 - GND
Notes:  | System Layout

## Slide 14
2. Troubleshooting
2.3 Trouble Shooting
Error No. 11002
• Symptom : System shutdown with displaying code 1002 on the main module SSD. (11002 on the Carel controller or Web UI)
• Cause : The float switch is opened due to rising of condensate water level, drain pump fault or drain pipe clogging
• Trouble shooting
- Follow the flow chart.
Clean the pipe
Is a drain pan filled half-way with water?
Is drain pipe clogged?
Is the output of the float switch shorted?
Check the slope of the
drain pan.
Check connection or
Replace main module
Yes
No
Yes
No
Yes
Replace float switch
No
[Float Switch Connection]
Float Switch Input
DI3 - GND
[Float Switch Check]
Float Switch
Condensate Water
Low Position = Short → 0 ohm
High Position = Open
Notes:  | System Layout

## Slide 15
2. Troubleshooting
2.3 Trouble Shooting
Error No. 11006
• Symptom : System keeps operating with displaying code 1006 on the main module SSD. (11006 on the Carel controller or Web UI)
• Cause : Pressure switch for the filters is activated.
• Trouble shooting : Check the filter condition
• Note : Differential Pressure switch for filter is not default(Factory Assembled), Need to buy and install 3rd party D/P Switch.
Check if there is any blockage on the filter
- It is recommended to check the filter once a month.
2. Clean or replace the filter if necessary.
3rd party Differential Pressure Switch for filter
Notes:  | System Layout

## Slide 16
2. Troubleshooting
2.3 Trouble Shooting
Error No. 11011
• Symptom : System shutdown with displaying code 1011 on the main module SSD. (11011 on the Carel controller or Web UI)
• Cause : The outdoor unit does not respond to DOAS command for 3 minutes.
• Trouble shooting
2. Check the connection with outdoor units based on the wiring diagram
[Wiring Diagram]
1. Check the Communication Indication LED - It will blink as often as transmission and reception is happened. - Green LED indicates transmission and yellow LED indicates reception from the main module.
[Communication Indication LED]
Notes:  | System Layout

## Slide 17
2. Troubleshooting
2.3 Trouble Shooting
Error No. 11012
• Symptom : System shutdown with displaying code 1012 on the main module SSD. (11012 on the Carel controller or Web UI)
• Cause : The outdoor unit is not compatible with DOAS system due to version mismatch.
• Trouble shooting
2. Update the main PCBA software of the outdoor unit
-. Compact DOAS Application with MV 5 system is available after SW version 1.47.0
1. Check the outdoor unit production date
ODU SW Version | SW Check Sum | Description | Production Date (ODU)
v1.49.0 | 2291 | 1. LG DOAS function updated ▪ LG Compact DOAS model can be connected to ODU. ▪ Model: ARND203DCR4, ARND153DCR4, ARND093DCR4 | `21. 6. 3 (2107)
Notes:  | System Layout

## Slide 18
• Symptom : System shutdown with displaying code below on the main module SSD (Carel controller or Web UI).
• Cause : The module inside control box does not respond to DOAS command for 3 seconds.
• Trouble shooting
2. Troubleshooting
2.3 Trouble Shooting
Error No. 11013 / 11014 / 11015 / 11021 / 11022 / 11023 / 11024
2. Check the connection with the modules based on the wiring diagram
Check the Communication Indication LED on each module. Main Module / UI Module / NTC Module / EEV Module
- It will blink as often as transmission and reception is happened. - Green LED indicates transmission and yellow LED indicates reception from the main module.
Fan PCB
- One Green LED Blinks when it transmits data.
1013 (11013) : UI module
1014 (11014) : NTC module
1015 (11015) : Fan communication board
1021 (11021) : Main_1 EEV module
1022 (11022) : Reheat EEV module
[Communication Indication LED]
[Wring Diagram]
Main Module
UI / NTC / EEV
Module
Fan CM
Board
Notes:  | System Layout

## Slide 19
• Cause : The 0~10V voltage type sensor’s input is not readable. (less than 0.1V or more than 9.9V)
If only the Sensor setting on Web UI(Configuration) was set to "Installed" without sensors.
• Trouble shooting
2. Troubleshooting
2.3 Trouble Shooting
Error No. 11112 / 11113 / 11114 / 11115 / 11118 / 11123 / 11124
2. Check the power supply to the sensor and sensor signal by using multi-tester. - If the voltage is not normal, pull out the signal cable from the module and check again.
1. In case of the 3rd party sensor installation, match the configuration on the Web UI. - If the sensors are not installed, the ‘Installed’ item on the configuration should set as Gray which is meaning “ Not Installed”
1112 (11112) : OA humidity (Factory assembled)
1113 (11113) : SA temperature (3rd party installation)
1114 (11114) : SA humidity (3rd party installation)
1115 (11115) : Differential pressure Sensor(3rd party installation)
1118 (11118) : CO2 Sensor (3rd party installation)
1123 (11123) : Space temperature (3rd party installation)
1124 (11124) : Space humidity (3rd party installation)
• Symptom : System keeps operating with displaying code below on the main module SSD (Carel controller or Web UI).
(e.g. Space Humidity Sensor setting on Web UI)
- Sensor is NOT installed -
- Sensor is installed -
Notes:  | System Layout

## Slide 20
2. Troubleshooting
2.3 Trouble Shooting
Error No. 11112 / 11113 / 11114 / 11115 / 11118 / 11123 / 11124
[Wiring Diagram for 0~10V type Sensor]
1. Is 24VAC power supplied to the sensor?
2. Check the sensor signal by using multi-tester.
3. If voltage is less than 0.1V or more than 9.9V, then pull out the signal
cable from the Main or UI module and check again without external
disturbance.
Notes:  | System Layout

## Slide 21
• Symptom : System keeps operating with displaying code below on the main module SSD (Carel controller or Web UI).
2. Troubleshooting
2.3 Trouble Shooting
Error No. 11131 / 11133 / 11134 / 11135 / 11137 / 11138
• Cause : The sensor connected to NTC module has a fault.
• Trouble shooting
2. Check the sensor resistance. a) Disconnect sensor wiring from NTC module
b) Set the multi-tester to resistance mode
c) Measure the resistance at the sensor outlet
d) If the value is more than 100kohm or less than 100ohm, sensor needs to be replaced.
※ Normal Value
- 10kohm at 77⁰F with ±5% tolerance
- 20kohm at 77⁰F
- 3.4kohm at 122⁰F
1. Check the connection to the NTC module.
1131 (11131) : Space temperature (3rd party installation)
1133 (11133) : OA temperature (Factory Assembled)
1134 (11134) : Main coil leaving air temperature_1 (Factory Assembled)
1135 (11135) : Main coil leaving air temperature_2 (Factory Assembled)
1137 (11137) : SA temperature (Factory Assembled)
1138 (11138) : Mix temperature (Factory Assembled)
Mix_Temp
SA_Temp
Leaving_Temp_2
Leaving_Temp_1
OA_Temp
SP/RA_Temp
Notes:  | System Layout

## Slide 22
• Symptom : System shutdown or keeps operating with displaying code below on the main module SSD (Carel controller or Web UI).
2. Troubleshooting
2.3 Trouble Shooting
Error No. 12102 / 12106 / 12202 / 12206
• Cause : Refrigerant temperature sensors connected to EEV module has a fault.
• Trouble shooting
2. Check the sensor resistance. a) Disconnect sensor wiring from NTC module
b) Set the multi-tester to resistance mode
c) Measure the resistance at the sensor outlet
d) If the value is more than 100kohm or less than 100ohm, sensor needs to be replaced.
※ Normal Value
- 5kohm at 77⁰F with ±5% tolerance
- 10kohm at 77⁰F
- 1.8kohm at 122⁰F
1. Check the connection to the EEV module.
Shutdown
2102 (12102) : Pipe-In temperature of Main Coil #1
2106 (12106) : Pipe-Out temperature of Main Coil #1
Keep Operating
2202 (12202) : Pipe-In temperature of Reheat Coil
2206 (12206) : Pipe-Out temperature of Reheat Coil
Pipe In
Pipe Out
Pipe In
Pipe Out
[NTC 5kohm sensor]
Notes:  | System Layout

## Slide 23
• Symptom : System shutdown or keeps operating with displaying code below on the main module SSD (Carel controller or Web UI).
2. Troubleshooting
2.3 Trouble Shooting
Error No. 12105 / 12205 /
• Cause : EEV modules do not communicate with outdoor unit.
• Trouble shooting
1. Check the communication indication LED (5th from the left) on the EEV module.
- When this green LED blinks, EEV module transmits data. (Communication speed is 1200bps.)
Shutdown
2105 (12105) : Communication error between ODU and Main Coil #1
Keep Operating
2205 (12205) : Communication error between ODU and Reheat Coil
2. Check the connection of the wiring for communication with ODU.
[Communication Indication LED]
[EEV Module]
[Internal Wiring Diagram for communication with ODU]
[Wiring Diagram]
Notes:  | System Layout

## Slide 24
2. Troubleshooting
2.3 Trouble Shooting
Error No. 170xx (SA fan driver fault)
Error Code | Level | Cause | Defect Assumption | Trouble Shooting
21 | 1 | IPM HW Fault |  | EC Motor is integrated with Inverter PCB Needs to exchange EC Motor assembly
23 | 1 | DC Link voltage is too low or too high |  | 
26 | 1 | Motor internal cable is disconnected |  | 
29 | 1 | Motor driving current is too high |  | 
40 | 1 | Bad component on current detection |  | 
52 | 1 | Fan communication PCBA doesn’t receive response from the EC Motor for 30 seconds | Losing communication or PCBA fault | There are Orange and Yellow LEDs indicate communication status. Orange will blink when fan communication PCBA transmits data to EC Motor and Yellow will blink when response is happened. (For this RS-232 communication, fan communication PCBA is master and EC motor is slave.)
57 | 1 | EC Motor doesn’t receive command for more than 3 minutes. |  | EC Motor is integrated with Inverter PCB Needs to exchange EC Motor assembly
62 | 1 | Heatsink Temp is over the spec |  | 
67 | 1 | Fan Motor is locked |  | Check if error occur after power reset Check whether fan blade is locked and fan blade turn smoothly when turned by hand
Notes:  | System Layout