Guide Specifications

# PRODUCT(S) - Indoor Units (Variable Refrigerant Flow Systems)

## Ducted – High Static <ZRNU073M2AA><ZRNU093M2AA><ZRNU123M2AA><ZRNU153M2AA><ZRNU183M2AA><ZRNU243M2AA><ZRNU283M3AA><ZRNU363B8AA><ZRNU423B8AA><ZRNU483B8AA><ZRNU543B8AA><ZRNU763B8AA><ZRNU963B8AA>

### General

#### Unit shall be manufactured by LG.

#### Unit shall be designed to be installed for indoor applications.

#### Unit shall be designed to mount fully concealed above the finished ceiling.

#### Unit shall have an opening to supply air from front horizontal and a dedicated rear horizontal return.

#### The supply air shall be flanged for field installed ductwork that shall not exceed the external static pressure limitation of the unit.

### Casing/Panel

#### Unit case shall be manufactured using galvanized steel plate.

#### The cold surfaces of the unit shall be covered internally with a coated polystyrene insulating material.

#### The cold surfaces of the unit shall be covered externally with sheet insulation made of Ethylene Propylene Diene Monomer (M-Class) (EPDM)

#### The external insulation shall be plenum rated and conform to ASTM Standard D-1418.

#### Unit shall be provided with hanger brackets designed to support the unit weight on four corners.

#### Hanger brackets shall have pre-punched holes designed to accept field supplied, all thread rod hangers.

### Cabinet Assembly

#### Unit shall have horizontal supply air discharge outlets and a return air inlet

#### Unit shall be equipped with factory installed temperature thermistors for:

##### Return air

##### Refrigerant entering coil

##### Refrigerant leaving coil

#### Unit shall have a factory assembled, piped and wired electronic expansion valve (EEV) for refrigerant control.

#### Unit shall have a built-in control panel to communicate with other indoor units and to the outdoor unit.

#### Unit shall have the following functions as standard:

##### Self-diagnostic function

##### Auto addressing

##### Auto restart function

##### Auto changeover function (Heat Recovery system only)

##### Auto operation function

##### Child lock function

##### Forced operation

##### Dual thermistor control

##### Sleep mode

##### External static pressure (ESP) control

##### Dual set point control

##### Multiple aux heater applications

##### Filter life timer

##### External on/off input

##### Wi-Fi compatible

##### Auto fan operation

##### Leak detection logic

### Fan Assembly

#### The unit shall have one or two direct drive Sirocco fans made of high strength ABS GP-2200 polymeric resin.

#### The fan impeller shall be statically and dynamically balanced.

#### The fans shall be mounted on a common shaft.

#### The fan motor is Brushless Digitally commutated (BLDC) with permanently lubricated and sealed ball bearings.

#### The fan motor shall include thermal, overcurrent and low RPM protection.

#### The fan/motor assembly shall be mounted on vibration attenuating rubber grommets.

#### The fan speed shall be controlled using microprocessor based direct digitally controlled algorithm that provides a minimum of three pre-programed fan speeds, each setting is also adjustable by field setting to compensate for a limited amount of additional resistance to airflow by adjusting the RPM of the fan motor.

#### In cooling mode, the indoor fan shall have the following settings; Low, Med, High, and Auto.

#### In heating mode, the indoor fan shall have the following settings: Low, Med, High, and Auto.

#### Each of the settings can be field adjusted from the factory setting (RPM/ESP).

#### Unit shall be designed for high speed air volume against an external static pressure of up to 0.98” water gauge, model dependent.

### Filter Assembly

#### The return air inlet shall have a factory supplied removable, washable filter. MERV 13 filter rack is available as an option, model dependent.

#### The filter access shall be from the rear of the unit.

### Coil Assembly

#### Unit shall have a factory built coil comprised of aluminum fins mechanically bonded on copper tubing.

#### The copper tubing shall have inner grooves to expand the refrigerant contact surface for high efficiency heat exchanger operation.

#### Unit shall have a minimum two to three row coil, 18-19 fins per inch.

#### Unit shall have a factory supplied condensate drain pan below the coil constructed of HIPS (high impact polystyrene resin).

#### Unit shall include an installed and wired condensate drain lift pump capable of providing a minimum of 27.5 inches of lift from the bottom surface of the unit. The unit drain pan is supplied with a secondary drain port/plug allowing the pan to be gravity drained and serviced.

#### The drain pump shall have a safety switch to shut off the unit if condensate rises too high in the drain pan, model dependent.

#### Unit shall have provision of 45° flare refrigerant pipe connections.

#### The coil shall be factory pressure tested at a minimum of 626 psig.

#### All refrigerant piping from outdoor unit to indoor unit shall be field insulated. Each pipe should be insulated separately. Thickness and heat transfer characteristics shall be determined by the design engineer and shall meet all code requirements.

### Microprocessor Control

#### The unit shall have a factory installed microprocessor controller capable of performing functions necessary to operate the system with or without the use of a wall mounted controller. The unit shall have a factory mounted return air thermistor for use as a space temperature control device. All operating parameters except scheduling shall be stored in non-volatile memory resident on the microprocessor. The microprocessor shall provide the following functions, self-diagnostics, auto re-start after a power failure, and a test run mode.

#### The unit shall be able to communicate with other indoor units and the outdoor unit using a field supplied minimum of 18 AWG, two core, stranded, twisted, and shielded communication cable.

#### The unit controls shall operate the indoor unit using one of the five operating modes:

##### Auto changeover (Heat Recovery System only)

##### Heating

##### Cooling

##### Dry

##### Fan only

#### The unit shall be able to operate in either cooling or heating mode for testing and/or commissioning.

#### The unit shall be able to operate with the fan turned off during system cooling thermal off.

#### The unit shall be able to operate with a continuous fan setting.

#### The unit shall have adjustable, multi-step cooling and heating mode thermal on/off temperature range settings.

#### The system shall include a product check function to access and display indoor unit type and capacity from a wired programmable thermostat controller.

#### The indoor unit shall have a factory installed R32 refrigerant leak detection sensor designed to communicate with mitigation devices and 3rd party alarms and transmit a system error code upon detection of a refrigerant leak or sensor failure/expiration.

#### An optional single-port shutoff valve shall be available as an additional accessory.  The shutoff valve shall be designed to integrate with and respond to a signal from a connected R32 refrigerant leak detection sensor, to close the refrigerant valve upon receiving a signal that a refrigerant leak has been detected, or that the sensor has incurred a failure or reached its 10-year expiration date.

### Electrical

#### The unit electrical power shall be 208-230/1/60 (V/Ph/Hz).

#### The unit shall be capable of operating within voltage limits of +/- 10% of the rated voltage.

### Controls

#### Unit shall use controls provided by the manufacturer to perform all functions necessary to operate the system effectively and efficiently and communicate with the outdoor unit over an RS-485 daisy chain.

#### The indoor unit shall have a factory installed R32 refrigerant leak detection sensor.

#### An optional single-port shutoff valve shall be available as an additional accessory.

### Seismic Installations

#### Provide with submittal: 1) OSHPD Special Seismic Certification Preapproval (OSP) documents for certified product list of VRF equipment to be installed in high seismic risk areas. 2) Equipment installation documents in conformance with CBC 2013, 2016 and 2019 California Building Code and IBC 2012, 2015 and 2018 International Building Code.

### Warranty

#### Please refer to the respective outdoor unit for applicable warranty.